## Dashboard
Water Calculators
Pressure Testing PE Pipe
The Pressure Testing PE Pipe calculator assists in calculating the acceptance formulas provided in the MRWA Water Code and can quickly confirm if the test results are satisfactory.
Open Calculator
Acknowledgments: City West Water, Yarra Valley Water
Thrust Anchorages for Water Mains (Project)
The Thrust Anchorage for Water Mains (Project) calculator assists the designer in finding the required thrust anchorage for all locations on their project.
Open Calculator
Acknowledgments: City West Water
Thrust Anchorages for Water Mains (Individual)
The Thrust Anchorage for Water Mains (Individual) calculator assists the designer in finding the required thrust anchorage fora single location, giving more detailed information on the dimensions of the thrust block.
Open Calculator
Acknowledgments: South East Water
PE Shrinkage Restraint
The PE Shrinkage Restraint calculator supplements the MRWA Water Code Standard Drawing MRWA-W-205A and assists the designer in calculating the required thrust restraint area for PE Shrinkage.
Open Calculator
Acknowledgments: City West Water
Restrained Main Length
The Restained Main Length calculator supplements the MRWA Water Code Standard Drawing MRWA-W-207 and assists the designer in calculating lengths L & l.
Open Calculator
Acknowledgments: City West Water
Calculator Style Guide
| Input | Insert values in these fields, some fields may have drop down boxes or display notes when selected.
| Calculation | Calculations based on the input will be displayed in these fields, important results will be displayed in bold.
| Constant | Formula constants are kept in these fields, contants may sometime need to be changed depending on the project or material type.
Version Control
| Version: | 1.9
Latest:
Please enable data connections to check for potential updates
MRWA Water Design Calculators - V1.9 (27/11/2016)

## Pressure Testing PE Pipe
Pressure Testing PE Pipe | [7 empty] | Menu
| Water Added During / At End Of: |  |  |  | PE Pipe Data
| 1st hour | 0 | litres |  | Length | 0 | km
| 2nd hour | 0 | litres |  | Diameter (External) | 125 | mm
| 3rd hour | 0 | litres |  | Average Test Head | 0 | metres head
| 4th hour | 0 | litres
| 5th hour | 0 | litres
Test Results
| Test passes if: | ∆V(5th hour) | ≤ | 0.55 x ∆V(3rd hour) + Vall
|  | 0 | ≤ | 0.55 x (0) + (0.14 x 0 x 0.125 x 0)
|  | 0 | ≤ | 0
|  | Test result: | PASS
Test Shut Off Blocks (SOBs) which contain PE pipes of varying diameter . For test SOBs containing <DN63PE pipe, discount this smaller diameter pipework in the PE test calculations. If there are no PE mains >DN63PE in the test SOB, test the SOB with the No Loss pressure testing method. Where there is more than one diameter of PE mains >DN63PE in the network to be tested, firstly try to separate the different diameter PE mains into separate Test SOBs. Where this is not practical, calculate the length weighted average diameter (Da) which = (L1D1 + L2D2 + L3D3) / ( L1 + L2 + L3). Then select the diameter in the PE pressure test calculator which is closest to Da. Where the selected diameter in the calculator is less than Da and the pressure test is a close fail, refer the matter to the water agency who will be able to change the calculator to insert the actual value of Da (rather than a standard PE pipe diameter).
Test SOBs which contain significant amounts of both PE and non PE mains. Where the Water Code specifies that a PE pressure test is required, it is acceptable to first attempt a No Loss Test (as the No Loss test is a higher standard) as follows: • Keep the pipeline at or within 10% of the test pressure for 12 hours, • Bring the main up to test pressure, • Undertake a 15 minute No Loss test, • If the pressure drops (by more than a few kPa), commence the full 5 hours pressure test in accordance with clause 19.4.1.1. The water agency will not record the unsuccessful attempt of the 15 minute No Loss test as a failure. • The formal result for the pressure test will either be a No Loss test pass, a 5 hour PE test pass or a 5 hour PE test fail.
Interpreting the equations: The procedure below refers to "DV (5hr - 4hr)". This is the amount of water added at the end of or during the 5th hour. Some testers add water regularly to maintain the pressure and sum the total amount added during the fifth hour. Some testers only add water at the end of the 5th hour. Either method is acceptable. Likewise, "DV (3hr-2hr)" is the amount of water added at the end of or during the 3rd hour.
MRWA Water Design Calculators - V1.9 (27/11/2016)

## Concrete Thrust Anchorage(Proj)
Thrust Anchorages for Water Mains (Project) | [8 empty] | Menu
Project Variables
|  |  | Enter the Soil Bearing Pressure for this site, in kPa: | 50 |  |  | Design Pressure for this site in metres: | 95
|  |  | Enter Top Water Level (TWL): | 80 |  |  | Test Pressure Safety Factor: | 1.25
|  |  | Enter Allowance for Surge in metres: | 20 |  |  | Minimum Hydrostatic Test Pressure, in kPa: | 1000
|  |  | Enter Lowest RL or RL where Thrust Restraint is required: | 5 |  |  | Test Pressure (kPa): | 1187.5
Tees & Dead Ends
For tees, use the diameter of the offtake.
| Location Label | Nominal Pipe Diameter | Test Pressure (kPa) | Pipe Outside Diameter (mm) | Resultant thrust (kN) | Required Thrust Area (m²)
|  | 100 | 1187.5 | 122 | 13.6096 | 0.27219
|  | 150 | 1187.5 | 177 | 28.6465 | 0.57293
|  | 225 | 1187.5 | 259 | 61.3372 | 1.2267
|  | 300 | 1187.5 | 345 | 108.8335 | 2.1767
|  | 375 | 1187.5 | 426 | 165.9371 | 3.3187
|  | 450 | 1187.5 | 507 | 235.0392 | 4.7008
|  | 600 | 1187.5 | 667 | 406.7954 | 8.1359
|  | 750 | 1187.5 | 826 | 623.8561 | 12.4771
Valves
Min concrete thrust restraint area is 0.3 m2. Timber / Recycle block is not practical.
| Location Label | Nominal Pipe Diameter | Test Pressure (kPa) | Outside dia. of pipe (mm) | Resultant thrust (kN) | Required Thrust Area (m²)
|  | 100 | 1187.5 | 122 | 13.6096 | 0.3
|  | 150 | 1187.5 | 177 | 28.6465 | 0.57293
|  | 225 | 1187.5 | 259 | 61.3372 | 1.2267
|  | 300 | 1187.5 | 345 | 108.8335 | 2.1767
|  | 375 | 1187.5 | 426 | 165.9371 | 3.3187
|  | 450 | 1187.5 | 507 | 235.0392 | 4.7008
|  | 600 | 1187.5 | 667 | 406.7954 | 8.1359
|  | 750 | 1187.5 | 826 | 623.8561 | 12.4771
Bends
| Location Label | Nominal Pipe Diameter | Deflection angle (x°) | Test Pressure (Kpa) | Outside dia. of pipe (mm) | Resultant thrust (kN) | Required Thrust Area (m²)
|  | 100 | 11.25 | 1187.5 | 122 | 2.6679 | Timber Block
|  | 100 | 22.5 | 1187.5 | 122 | 5.3102 | Timber Block
|  | 100 | 30 | 1187.5 | 122 | 7.0448 | Timber Block
|  | 100 | 45 | 1187.5 | 122 | 10.4163 | 0.20833
|  | 100 | 90 | 1187.5 | 122 | 19.2468 | 0.38494
|  | 150 | 11.25 | 1187.5 | 177 | 5.6157 | Timber Block
|  | 150 | 22.5 | 1187.5 | 177 | 11.1773 | 0.22355
|  | 150 | 30 | 1187.5 | 177 | 14.8285 | 0.29657
|  | 150 | 45 | 1187.5 | 177 | 21.925 | 0.4385
|  | 150 | 90 | 1187.5 | 177 | 40.5122 | 0.81024
|  | 225 | 11.25 | 1187.5 | 259 | 12.0242 | 0.24048
|  | 225 | 22.5 | 1187.5 | 259 | 23.9326 | 0.47865
|  | 225 | 30 | 1187.5 | 259 | 31.7505 | 0.63501
|  | 225 | 45 | 1187.5 | 259 | 46.9455 | 0.93891
|  | 225 | 90 | 1187.5 | 259 | 86.7439 | 1.7349
Tapers &/Or Reducers
Min concrete thrust restraint area is 0.3 m2. Timber / Recycle block is not practical.
| Location Label | Diam Larger Pipe | Diam Smaller Pipe | Test Pressure (kPa) | Outside dia. of larger pipe (mm) | Outside dia. of smaller pipe (mm) | Resultant thrust (kN) | Required Thrust Area (m²)
|  | 150 | 100 | 1187.5 | 177 | 122 | 15.0369 | 0.30074
|  | 225 | 100 | 1187.5 | 259 | 122 | 47.7276 | 0.95455
|  | 225 | 150 | 1187.5 | 259 | 177 | 32.6907 | 0.65381
|  | 300 | 100 | 1187.5 | 345 | 122 | 95.2239 | 1.9045
|  | 300 | 150 | 1187.5 | 345 | 177 | 80.187 | 1.6037
|  | 300 | 225 | 1187.5 | 345 | 259 | 47.4963 | 0.94993
Thrust Block Dimensions
To determine (L)ength and (H)eight proportions use formula L=√A/0.6
( Height based on 60% of length, this figure may be varied)
| Where: | L=L(m)
H=0.6L(m)
A=Thrust Area (m2)
MRWA Water Design Calculators - V1.9 (27/11/2016)

## Concrete Thrust Anchorage(Ind)
Thrust Anchorages for Water Mains (Individual) | [6 empty] | Menu
| Anchour Block Details |  |  |  | Tees & Bends Thrust Block Dimension Guide
|  | Design Pressure (m) | 50 |  | Width (mm)* | 250
*Depends on the Excavation. Typically 250mm
|  | Soil Type | Stiff Clay (50 kPa)
[5 empty] | Length (mm) | 618.0798
|  | Fitting Type | Tee or Dead End
[5 empty] | Height (mm) | 370.8479
|  | Fitting DN | 100
|  | Select the larger size for Tapers |  |  | Volume (m³) | 0.057303
|  | Deflection Angle (°)* | 90
|  | *Only applicable when Fitting Type = Bends |  |  | Note: 1. Volume calculated is based on a rectangular shape with the 250mm width. 2. Length and height calculated so that the height is 60% of the length of the block.
|  | Smaller DN | 100
|  | Test Pressure (m) | 100
|  | Resultant Thrust (kN) | 11.4607
|  | Thrust Area (m²) | 0.22921
|  | Thrust Material | Concrete
Calculations based on WSA03-2011
Extract from MRWA-W-205A
MRWA Water Design Calculators - V1.9 (27/11/2016)

## PE Shrinkage Restraint
PE Shrinkage Restraint | [10 empty] | Menu
Project Variables
|  | Test Pressure (P): | 1000 | kPa
|  | PE Pipe OD (D): | 280 | mm
|  | Pipe Temp at Time of Connection (T1): | 25 | deg C
|  | Length of Main (L): | 100 | m
|  | AHBP: | 50 | kPa
Constants
|  | PE Pipe OD: | 280 | mm
|  | SDR: | 11
|  | Poisson's ratio (µ): | 0.4
|  | Average ground temperature (T2): | 16 | deg C
|  | Co-efficient of expansion (K): | 0.00018 | m/ deg/ m
|  | 2 yr Youngs Modulus (E): | 900000 | kPa
|  | Factor of Safety: | 1.5
| Shut Valve Force |  |  |  | Thrust Restraint Area
|  | Fl = | 61.5752 | kN |  | Change in Length (∆L) = | -206.4444 | mm | (-ve denotes PE main shrinkage)
| Poisson's Effect |  |  |  | PE Shrinkage Restraint IS NOT required when change of length is > -20mm
|  | A = (1/SDR)-(1/SDR2) = | 0.082645 |  |  | Area (Valve Contribution) = | 1.8473 | m²
|  | B = P(SDR-1)/2 = | 5000 |  |  | Area (Poisson's Effect Contribution) = | 1.2207 | m²
|  | C = µ*p*D2 = | 98470.4 |  |  | Area (Thermal Expansion Contribution) | 0.90748 | m²
|  | ∆L1 =(L*µ*P)/E | -44.4444 | mm |  | Total Net Area (valved)= | 2.7547 | m²
|  | Fr = A*B*C = | 40.6902 | kN |  | Total Net Area (not valved)= | 2.1282 | m²
Thermal Expansion
|  | Pipe Cross Section Area = | 0.020747 | m² | Summary Table
Valid for: DN280PE; 50 AHBP; 1000 kPa Test Pressure
|  | ∆L2 = L*K*(T1-T2) = | -162 | mm
Pipe Temp at Time of Connection
|  | Ft = (T1-T2)*K*E*A = | 30.2492 | kN |  |  | 20 | 25 | 30 | 35
[5 empty] | Restraint Area (Valved) (m²) |  | 2.2506 | 2.7547 | 3.2589 | 3.763
| Net Maximum Force |  |  |  | Restraint Area (Not Valved) (m²) |  | 1.624 | 2.1282 | 2.6323 | 3.1365
|  | Force (net maximum) = | 91.8245 | kN
MRWA Water Design Calculators - V1.9 (25/11/2016)

## Restrained Main Lengths
Restrained Main Lengths | [5 empty] | Menu
| FOR DUCTILE IRON PIPE | [5 empty] | FOR PE PIPE
| Project Variables | [5 empty] | Project Variables
|  |  | Test Pressure | 1600 | kPa |  |  |  | Test Pressure | 1600 | kPa
|  |  | Cover | 450 | mm |  |  |  | Cover | 450 | mm
|  | Cover |  | 0.45 | m |  |  | Cover |  | 0.45 | m
|  | Passive Soil P | [5 empty] | Passive Soil P
|  | Nthi=Tan^2(45deg+Thi/2) |  | 3 |  |  |  | Nthi=Tan^2(45deg+Thi/2) |  | 3
|  | Pipe Friction Angle | Thi x Fthi | 22.5 | deg |  |  | Pipe Friction Angle | Thi x Fthi | 22.5 | deg
| Bends | [5 empty] | Bends
|  |  | Angle of pipe bend | 90 | deg |  |  |  | Angle of pipe bend | 90 | deg
|  |  | DI Pipe DN | 100 |  |  |  |  | PE Pipe DN (OD) | 125 | mm
|  | Outside Diameter |  | 0.122 | m |  |  | Outside Diameter |  | 0.125 | m
|  | Cross Sec Area | PieD^2 / 4 | 0.01169 | m^2 |  |  | Cross Sec Area | PieD^2 / 4 | 0.012272 | m^2
|  | unit fric force |  | 1.1225 | kN/m |  |  | unit fric force |  | 1.1225 | kN/m
|  | Depth to Stringer |  | 0.511 | m |  |  | Depth to Stringer |  | 0.5125 | m
|  | Earth load | X x H xD | 0.87902 |  |  |  | Earth load | X x H xD | 0.87902
|  | Weight Pipe | Cross Area Pipe x D | 0.1725 | kN/m |  |  | Pipe ID |  | 0.101 | m
|  | Weight Water |  | 0.081713 | kN/m |  |  | Weight Pipe | Cross Area Pipe x D | 0.040683 | kN/m
|  | Wall Thickness x 2 |  | 0.01 | m |  |  | Weight Water |  | 0.080118 | kN/m
|  | Cement Thickness x 2 |  | 0.01 | m
|  |  |  | 21.6153 | [5 empty] | 21.6787
|  |  | Fitting thrust | 28.0557 | kN |  |  |  | Fitting thrust | 29.4524 | kN
|  |  | Friction Thrust Resistance per meter | 2.3752 | Horizonal |  |  |  | Friction Thrust Resistance per meter | 2.4097 | Horizonal
|  |  | Friction Thrust Resistance per meter | 1.1225 | vert down |  |  |  | Friction Thrust Resistance per meter | 1.1225 | vert down
|  |  | L (horizontal or vertical up bends) = | 11.8122 | m |  |  |  | L (horizontal or vertical up bends) = | 12.2223 | m
|  |  | L (vertical down bends) = | 24.9929 | m |  |  |  | L (vertical down bends) = | 26.2372 | m
| Dead Ends | [5 empty] | Dead Ends
|  | Depth to Stringer |  | 0.5385 | m |  |  | Depth to Stringer |  | 0.54 | m
|  | Earth load | X x H xD | 1.3439 |  |  |  | Earth load | X x H xD | 1.3705
|  | Unit Friction Force |  | 1.7499 | kN/m |  |  | Unit Friction Force |  | 1.6689 | kN/m
|  | Weight Pipe | Cross Area Pipe x Y | 0.25544 | kN/m |  |  | PE pipe ID |  | 0.146 | m
|  | Weight Water |  | 0.19359 | kN/m |  |  | Weight Pipe | Cross Area Pipe x Y | 0.083136 | kN/m
|  | Wall Thickness x 2 |  | 0.01 | m |  |  | Weight Water |  | 0.16742 | kN/m
|  | Cement Thickness x 2 |  | 0.01 | m
|  | Pipe Friction Angle | Thi x Fthi | 22.5 | deg |  |  | Pipe Friction Angle | Thi x Fthi | 22.5 | deg
|  |  | Fitting thrust | 59.0538 | kN |  |  |  | Fitting thrust | 61.0726 | kN
|  |  | Friction Thrust Resistance per meter | 1.7499 | kN/m |  |  |  | Friction Thrust Resistance per meter | 1.6689 | kN/m
|  |  | DI Pipe DN | 150 |  |  |  |  | PE Pipe DN (OD) | 180 | mm
|  | Outside Diameter |  | 0.177 | m |  |  | Outside Diameter |  | 0.18 | m
|  | Cross Sec Area | PieD^2 / 4 | 0.024606 | m^2 |  |  | Cross Sec Area | PieD^2 / 4 | 0.025447 | m^2
|  |  | L = | 33.7464 | m |  |  |  | L = | 36.5953 | m
| Tees | [5 empty] | Tees
| Assumes both straight main and offtake main are DI | [5 empty] | Assumes both straight main and offtake main are PE
|  |  | DI Pipe DN of straight main | 100 |  |  |  |  | PE Pipe DN (OD) of straight main | 125 | mm
|  | Outside Diameter of Run |  | 0.122 | m |  |  | Outside Diameter of Run |  | 0.125 | m
|  |  | DI Pipe Length of Restrained Run (straight main) | 10 | m |  |  |  | PE Pipe Length of Restrained Run (straight main) | 10 | m
|  | Depth to Stringer |  | 0.511 | m |  |  | Depth to Stringer |  | 0.5125 | m
|  |  |  | 21.6153 | [5 empty] | 21.6787
|  | Pipe Thrust Minus Straight Main Thrust Reisitance |  | 15.5296 | kN |  |  | Pipe Thrust Minus Straight Main Thrust Reisitance |  | 16.5807 | kN
|  |  | DI Pipe DN of Offtake | 100 |  |  |  |  | PE Pipe Offtake DN (OD) | 125 | mm
|  |  | DI Pipe DN of Offtake | 0.122 | m |  |  |  | PE Pipe Offtake DN (OD) | 0.125 | m
|  | Cross Sec Area | PipeOD^2 / 4 | 0.01169 | m^2 |  |  | Cross Sec Area | PipeOD^2 / 4 | 0.012272 | m^2
|  |  | Offtake Friction Thrust Resistance per meter | 1.1225 | kN/m |  |  |  | Offtake Friction Thrust Resistance per meter | 1.0752 | kN/m
|  | Depth to Stringer |  | 0.511 | m |  |  | Depth to Stringer |  | 0.5125 | m
|  | Earth load | X x H xD | 0.87902 |  |  |  | Earth load | X x H xD | 0.90328
|  | Weight Pipe | Cross Area Pipe x Y | 0.1725 | kN/m |  |  | Weight Pipe | Cross Area Pipe x Y | 0.040683 | kN/m
|  | Weight Water |  | 0.081713 | kN/m |  |  | Weight Water |  | 0.080118 | kN/m
|  | Wall Thickness x 2 |  | 0.01 | m |  |  | PE pipe ID |  | 0.101 | m
|  | Cement Thickness x 2 |  | 0.01 | m
|  | Pipe Friction Angle | Thi x Fthi | 22.5 | deg |  |  | Pipe Friction Angle | Thi x Fthi | 22.5 | deg
|  |  | Offtake Friction Thrust Resistance per meter | 1.1225 | kN/m |  |  |  | Offtake Friction Thrust Resistance per meter | 1.0752 | kN/m
|  |  | L (branch) = | 13.8343 | m |  |  |  | L (branch) = | 15.4213 | m
|  |  |  | If -ve number, no restraint for the branch is required. | [5 empty] | If -ve number, no restraint for the branch is required.
| Tapers | [5 empty] | Tapers
| Assumes both larger and smaller mains are DI & taper is valved | [5 empty] | Assumes both larger and smaller mains are PE & taper is valved
|  |  | DN of larger pipe | 225 |  |  |  |  | PE Pipe DN (OD) of larger main | 280 | mm
|  | Outside diameter of big pipe |  | 0.259 | mm |  |  | Outside diameter of big pipe |  | 0.28
|  | X section area big pipe |  | 0.052685 | m2 |  |  | X section area big pipe |  | 0.061575 | m2
|  |  | DN of smaller pipe | 100 |  |  |  |  | PE Pipe DN (OD) of smaller main | 125 | mm
|  | Outside diameter of small pipe |  | 0.122 | m |  |  | Outside diameter of small pipe |  | 0.125 | m
|  | X section area small pipe |  | 0.01169 | m2 |  |  | X section area small pipe |  | 0.012272 | m2
|  | Large Main | [5 empty] | Large Main
|  | Thrust resistance per m |  | 2.8229 | kN/m |  |  | Thrust resistance per m |  | 2.9371 | kN/m
|  | Depth to Stringer |  | 0.5795 | m |  |  | Depth to Stringer |  | 0.59 | m
|  | Earth load | X x H xD | 2.1163 |  |  |  | Earth load | X x H xD | 2.3293
|  | Weight Pipe | Cross Area Pipe x Y | 0.3791 | kN/m |  |  | Weight Pipe | Cross Area Pipe x Y | 0.19813 | kN/m
|  | Weight Water |  | 0.44863 | kN/m |  |  | Weight Water |  | 0.40828 | kN/m
|  | Wall Thickness x 2 |  | 0.01 | m |  |  | Pipe ID |  | 0.228 | m
|  | Cement Thickness x 2 |  | 0.01 | m
|  | Pipe Friction Angle | Thi x Fthi | 22.5 | deg |  |  | Pipe Friction Angle | Thi x Fthi | 22.5 | deg
|  | Hydraulic Thrust |  | 126.4447 | kN |  |  | Hydraulic Thrust |  | 147.7805 | kN
|  | Thrust resistance per m |  | 2.8229 | kN/m |  |  | Thrust resistance per m |  | 2.9371 | kN/m
|  |  | Length of bigger main to restrain | 44.7927 | m |  |  |  | Length of bigger main to restrain | 50.3148 | m
|  | Small Main | [5 empty] | Small Main
|  | Thrust resistance per m |  | 1.1225 | kN/m |  |  | Thrust resistance per m |  | 1.0868 | kN/m
|  | Cover |  | 0.45 | m |  |  | Cover |  | 0.45 | kN/m
|  | Depth to Stringer |  | 0.511 | m |  |  | Depth to Stringer |  | 0.5125 | m
|  | Earth load | X x H xD | 0.87902 |  |  |  | Earth load | X x H xD | 0.90328
|  | Weight Pipe | Cross Area Pipe x Y | 0.1725 | kN/m |  |  | Weight Pipe | Cross Area Pipe x Y | 0.040683 | kN/m
|  | Weight Water |  | 0.081713 | kN/m |  |  | Weight Water |  | 0.080118
|  | Wall Thickness x 2 |  | 0.01 | m |  |  | Pipe ID |  | 0.101 | m
|  | Cement Thickness x 2 |  | 0.01 | m
|  | Pipe Friction Angle | Thi x Fthi | 22.5 | deg |  |  | Pipe Friction Angle | Thi x Fthi | 22.5 | deg
|  | Hydraulic Thrust |  | 28.0557 | kN/m |  |  | Hydraulic Thrust |  | 29.4524 | kN
|  |  | Length of smaller main to restrain | 24.9929 | m |  |  |  | Length of smaller main to restrain | 27.0993 | m
| Assumptions / Constants Used & Notes | [5 empty] | Assumptions / Constants Used & Notes
|  | All length values shall be multiplied by a factor of 1.4 if pipework is wrapped in PE sleeve | [5 empty] | All length values shall be multiplied by a factor of 1.4 if pipework is wrapped in PE sleeve
|  | Pipe weight calculations based on Di pipe | [5 empty] | Pipe weight calculations based on Di pipe
|  | Pi | 3.1416 |  |  |  |  | Pi | 3.1416
|  | Factor of Safety | 1.5 |  |  |  |  | Factor of Safety | 1.5
|  | Pipe Cohesion | 0 | kN/m^2 |  |  |  | Pipe Cohesion | 0 | kN/m^2
|  | Soil Cohesion | 0 | kN/m^3 |  |  |  | Soil Cohesion | 0 | kN/m^3
|  | earth load desity | 14.1 | kN/m^3 |  |  |  | earth load desity | 14.1 | kN/m^3
|  | ductile iron load density | 71 | kN/m^3 |  |  |  | PE pipe density | 9.55 | kN/m^3
|  | cement load density | 25 | kN/m^3 |  |  |  | PE pipe SDR | 11
|  | water load density | 10 | kN/m^3 |  |  |  | water load density | 10 | kN/m^3
|  | soil friction angle | 30 |  |  |  |  | soil friction angle | 30
|  | ratio of pipe fric angle to soil fric angle | 0.75 |  |  |  |  | ratio of pipe fric angle to soil fric angle | 0.75
|  | Trench Type Modifier | 0.95 |  |  |  |  | Trench Type Modifier | 0.95
|  | Ductile iron wall thickness | 0.005 | m
|  | Cement Lining thickness | 0.005 | m
MRWA Water Design Calculators - V1.9 (27/11/2016)

## Settings
Calculator Settings
Fitting Type | Deflection Angle (°) | Pipe Size |  | Soil Types | AHBP(kPa) | Poly OD | Poly ID
Bend | 11.25 | DN | OD (mm) | Stiff Clay (50 kPa) | 50 | 125 | 101 | 8011.8467
Taper | 22.5 | 100 | 122 | Medium-Dense Clean Sand (50 kPa) | 50 | 180 | 146 | 16741.5473
Tee or Dead End | 30 | 125 | 144 | Very Stiff Clay (100 kPa) | 100 | 280 | 228 | 40828.1381
Valve | 45 | 150 | 177 | Dense Clean Sand / Gravel (100 kPa) | 100 | 315 | 256 | 51471.854
| 60 | 200 | 222 | Decomposed Rock (100 kPa) | 100 | 355 | 289 | 65597.24
| 90 | 225 | 259 | Hard Clay (200 kPa) | 200 | 400 | 325 | 82957.681
|  | 250 | 274 | Sound Rock (200 kPa) | 200 | 500 | 407 | 130100.4204
|  | 300 | 345 |  |  | 560 | 455 | 162597.0548
|  | 350 | 378 |  |  | 630 | 512 | 205887.4161
|  | 375 | 426
|  | 400 | 429
|  | 450 | 507
|  | 500 | 532
|  | 600 | 667
|  | 675 | 747
|  | 750 | 826
|  | 825 | 838
|  | 900 | 972
|  | 1050 | 1125
|  | 1150 | 1200
|  | 1200 | 1219
|  | 1350 | 1404
|  | 1700 | 1752
|  | 2100 | 2160